## Ingersoll
Date | Shift | Operator | Run Hours | Next service hrs | Oil Level | Oil Leaks | Air Leaks | Pressure (Bar) | Dew point (°C)(inbuilt) | Dew point (°C)(External) | Element Temp (°C) | Air Filter Condition | Prefilter condition | Condensate Drained | Alarms on Panel | Remarks/Actions Taken
2025-12-01 | D | Okiri | 11372 | 11602 | LOW | [10 empty] | standby
2025-12-02 | D | Okiri | 11372 |  | LOW | [10 empty] | standby
2025-12-03 | D | Okiri | 11372 |  | LOW |  |  |  | - | [6 empty] | standby
2025-12-04 | D | Okiri | 11372 |  | LOW | [10 empty] | standby
2025-12-05 | D | Okiri | 11372 |  | LOW | [10 empty] | standby
2025-12-06 | D | Okiri | 11372 |  | LOW | [10 empty] | standby
2025-12-07 | C | Benjamin | 11372 |  | LOW | [10 empty] | standby
2025-12-08 | C | Benjamin | 11372 |  | LOW | [10 empty] | standby
2025-12-09 | C | Benjamin | 11372 |  | LOW | [10 empty] | standby
2025-12-10 | C | Benjamin | 11372 |  | LOW | [10 empty] | standby
2025-12-11 | C | Benjamin | 11372 |  | LOW | [10 empty] | standby
2025-12-12 | C | Benjamin | 11372 |  | LOW
2025-12-13 | C | Benjamin | 11372 |  | LOW
2025-12-15 | B | Korir | 11372 |  | LOW

## Atlas Copco
Date | Shift | Operator Name | Run Hours | Next service hrs | Oil Level | Oil Leaks | Air Leaks | Pressure (Bar) | Dew point (°C)(inbuilt) | Dew point (°C)(External) | Element Temp (°C) | Air Filter Condition | Prefilter condition | Condensate Drained | Alarms on Panel | Remarks/Actions Taken
2025-12-01 | D | Okiri | 13704 | 13965 | Ok | No | No | 7 | 60 | 21 | 72 | Ok | Ok | Ok | Drier Dewpoint protection alarm | Auto drain repaired temporarily
2025-12-02 | D | Okiri | 13724 |  | Ok | No | No | 7 | 57 | 20 | 74 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-03 | D | Okiri | 13750 |  | OK | No | No | 7 | 63 | 23 | 72 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-04 | D | Okiri | 13778 |  | Ok | No | No | 7 | 63 | 18 | 74 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-05 | D | Okiri | 13799 |  | Ok | No | No | 7 | 64 | 21 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-06 | D | Okiri | 13823 |  | Ok | No | No | 7 | 62 | 20 | 72 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-07 | C | Benjamin | 13848 |  | Ok | No | No | 7 | 68 | 24 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm | Prefilter cleaned
2025-12-08 | C | Benjamin | 13872 |  | Ok | No | No | 7 | 60 | 20 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-09 | C | Benjamin | 13896 |  | Ok | No | No | 7 | 65 | 23 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-10 | C | Benjamin | 13919 |  | Ok | No | No | 7 | 65 | 21 | 72 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-11 | C | Benjamin | 13942 |  | Ok | No | No | 7 | 64 | 21 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm
2025-12-12 | C | Benjamin | 13970 |  | Ok | No | No | 7 | 60 | 18 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm | Overdue for service
2025-12-13 | C | Benjamin | 13989 |  | Ok | No | No | 7 | 62 | 18 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm | Overdue for service
2025-12-15 | B | Korir | 14042 |  | Ok | No | No | 7 | 53 | 19 | 73 | Ok | Ok | Ok | Drier Dewpoint protection alarm | Overdue for service

## EDG
Date | Shift | Operator Name | Last service date | Run Hours | Interval hrs | Next service hrs | Oil Level | Oil Leaks | Coolant level | Fuel level | Alarms on Panel | Remarks/Actions Taken
2025-12-01 |  |  | 2025-11-03 | 884.7 | 250 | 1134.7 | ok | NO | ok | 0.75
2025-12-02 |  |  | 2025-11-19 | 884.7 |  |  | ok | No | ok | 0.75
2025-12-05 | D | OKIRI |  | 887.4 | 250 | 1134.7 | ok | NO | ok | 0.75 |  | Not in auto with Grid
2025-12-11 | C | Benjamin |  | 887.4 |  |  | ok | NO | ok | 0.75 |  | Faulty, battery weak for start up without 230v supply

## Weekly_Monthly Checklist
Week/Month | Air Filter Condition | Oil Filter Condition | Separator Element | Drain System Function | Remarks/Actions Taken | Checked By | Date